## Pole Table
POLE AND STAY SET SCHEDULE - BAHUNDANDA SOUTH SPUR
Allowance for sag, jumpers and wastage (x distance): |  |  |  |  | 1.1 | template convention (+10 %); distances are already measured along slope
Node name |  | Reach name | Phase | Distance (km) | Distance (m) | Distance with sag (m) | Number of poles | Stay sets | No. of wires | Conductor length with sag (m) | Pole type
From | To
HT00 | T1 | HT00-T1 | 3 (11 kV) | 0.269 | 269 | 295.9 | 5 | 3 | 3 | 887.7 | 11 m STP
T1 | T1 | T1 structure | 3 (11 kV) | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 m STP x 2 (DP)
T1 | A08 | T1-A08 | 2 (y,b) | 0.264 | 264 | 290.4 | 8 | 7 | 3 | 871.2 | 8 m STP
A08 | A105 | A08-A105 | 1 (b) | 0.131 | 131 | 144.1 | 5 | 4 | 2 | 288.2 | 8 m STP
A08 | A207 | A08-A207 | 1 (y) | 0.2 | 200 | 220 | 7 | 6 | 2 | 440 | 8 m STP
T1 | B07 | T1-B07 | 1 (b) | 0.164 | 164 | 180.4 | 7 | 5 | 2 | 360.8 | 8 m STP
T1 | C07 | T1-C07 | 1 (r) | 0.148 | 148 | 162.8 | 7 | 5 | 2 | 325.6 | 8 m STP
C01 | C104 | C01-C104 | 1 (r) | 0.107 | 107 | 117.7 | 4 | 3 | 2 | 235.4 | 8 m STP
T1 | D06 | T1-D06 | 2 (r,y) | 0.191 | 191 | 210.1 | 6 | 1 | 3 | 630.3 | 8 m STP
D06 | D104 | D06-D104 | 1 (r) | 0.116 | 116 | 127.6 | 4 | 3 | 2 | 255.2 | 8 m STP
D06 | D204 | D06-D204 | 1 (y) | 0.127 | 127 | 139.7 | 4 | 3 | 2 | 279.4 | 8 m STP
D202 | D301 | D202-D301 | 1 (y) | 0.033 | 33 | 36.3 | 1 | 1 | 2 | 72.6 | 8 m STP
Total |  |  |  | 1.75 | 1750 | 1925 | 60 | 42 |  | 4646.4
Total 11 kV (line + T1 structure) |  |  |  | 0.269 | 269 | 295.9 | 7 | 4 |  | 887.7
Total LV two-phase |  |  |  | 0.455 | 455 | 500.5 | 14 | 8 |  | 1501.5
Total LV single-phase |  |  |  | 1.026 | 1026 | 1128.6 | 39 | 30 |  | 2257.2
Total LV (2-phase + 1-phase) |  |  |  | 1.481 | 1481 | 1629.1 | 53 | 38 |  | 3758.7
Check: totals vs sheet "Pole List" | [6 empty] | OK | OK
Steel tubular poles (STP) shall be used: 11 m for the 11 kV line and the T1 structure, 8 m for LV lines.
Notes
1. Distance = route length along slope from the desktop survey (same as on the SLD).
2. Number of poles in a reach = new poles after its start node up to and including its end node; the start node is counted in the upstream reach, so no pole is counted twice.
3. Stay sets follow the survey rule (see sheet "Pole List"); each pole is listed there with its function, stay sets, coordinates and elevation.
4. Wires: 11 kV three-phase = 3; LV two-phase = 3 (2 phases + neutral); LV single-phase = 2 (phase + neutral). Conductor size is fixed in the voltage-drop design.
5. Blue = survey input; black = formula; green = taken from sheet "Pole List"; yellow = assumption you can change.

## Pole List
POLE LIST
Pole ID | Reach | Line | Poles (nos) | Pole height (m) | Line deviation (deg) | Stay sets
HT00 | HT00-T1 | 11 kV | 1 | 11 | 0 | 1
HT01 | HT00-T1 | 11 kV | 1 | 11 | 41 | 1
HT02 | HT00-T1 | 11 kV | 1 | 11 | 6 | 0
HT03 | HT00-T1 | 11 kV | 1 | 11 | 2 | 0
HT04 | HT00-T1 | 11 kV | 1 | 11 | 31 | 1
T1 | T1 structure | 11 kV / transformer | 2 | 11 | 0 | 1
A01 | T1-A08 | LV | 1 | 8 | 0 | 0
A02 | T1-A08 | LV | 1 | 8 | 6 | 0
A03 | T1-A08 | LV | 1 | 8 | 23 | 1
A04 | T1-A08 | LV | 1 | 8 | 32 | 1
A05 | T1-A08 | LV | 1 | 8 | 42 | 1
A06 | T1-A08 | LV | 1 | 8 | 58 | 1
A07 | T1-A08 | LV | 1 | 8 | 63 | 2
A08 | T1-A08 | LV | 1 | 8 | 0 | 1
A101 | A08-A105 | LV | 1 | 8 | 20 | 1
A102 | A08-A105 | LV | 1 | 8 | 11 | 1
A103 | A08-A105 | LV | 1 | 8 | 11 | 1
A104 | A08-A105 | LV | 1 | 8 | 0 | 0
A105 | A08-A105 | LV | 1 | 8 | 0 | 1
A201 | A08-A207 | LV | 1 | 8 | 2 | 0
A202 | A08-A207 | LV | 1 | 8 | 34 | 1
A203 | A08-A207 | LV | 1 | 8 | 3 | 0
A204 | A08-A207 | LV | 1 | 8 | 68 | 2
A205 | A08-A207 | LV | 1 | 8 | 42 | 1
A206 | A08-A207 | LV | 1 | 8 | 15 | 1
A207 | A08-A207 | LV | 1 | 8 | 0 | 1
B01 | T1-B07 | LV | 1 | 8 | 75 | 2
B02 | T1-B07 | LV | 1 | 8 | 8 | 0
B03 | T1-B07 | LV | 1 | 8 | 4 | 0
B04 | T1-B07 | LV | 1 | 8 | 4 | 0
B05 | T1-B07 | LV | 1 | 8 | 11 | 1
B06 | T1-B07 | LV | 1 | 8 | 18 | 1
B07 | T1-B07 | LV | 1 | 8 | 0 | 1
C01 | T1-C07 | LV | 1 | 8 | 0 | 1
C02 | T1-C07 | LV | 1 | 8 | 8 | 0
C03 | T1-C07 | LV | 1 | 8 | 31 | 1
C04 | T1-C07 | LV | 1 | 8 | 9 | 0
C05 | T1-C07 | LV | 1 | 8 | 18 | 1
C06 | T1-C07 | LV | 1 | 8 | 20 | 1
C07 | T1-C07 | LV | 1 | 8 | 0 | 1
C101 | C01-C104 | LV | 1 | 8 | 32 | 1
C102 | C01-C104 | LV | 1 | 8 | 21 | 1
C103 | C01-C104 | LV | 1 | 8 | 10 | 0
C104 | C01-C104 | LV | 1 | 8 | 0 | 1
D01 | T1-D06 | LV | 1 | 8 | 9 | 0
D02 | T1-D06 | LV | 1 | 8 | 0 | 0
D03 | T1-D06 | LV | 1 | 8 | 0 | 0
D04 | T1-D06 | LV | 1 | 8 | 0 | 0
D05 | T1-D06 | LV | 1 | 8 | 0 | 0
D06 | T1-D06 | LV | 1 | 8 | 0 | 1
D101 | D06-D104 | LV | 1 | 8 | 9 | 0
D102 | D06-D104 | LV | 1 | 8 | 33 | 1
D103 | D06-D104 | LV | 1 | 8 | 52 | 1
D104 | D06-D104 | LV | 1 | 8 | 0 | 1
D201 | D06-D204 | LV | 1 | 8 | 1 | 0
D202 | D06-D204 | LV | 1 | 8 | 0 | 1
D203 | D06-D204 | LV | 1 | 8 | 10 | 1
D204 | D06-D204 | LV | 1 | 8 | 0 | 1
D301 | D202-D301 | LV | 1 | 8 | 0 | 1
Total |  |  | 60 |  |  | 42
Stay-set rule: 1 at each dead-end, 1 per tee-off branch, 1 at angles 10-60 deg, 2 at angles > 60 deg; HT tap-off and HT terminal (T1) 1 each.